## Pump_Calculation
Category | Parameter | Value | Unit | Formula/Note
INPUT | Fluid Density (rho) | 1000 | kg/m3 | At operating temperature
INPUT | Operating Temp | 40 | C
INPUT | Vapor Pressure (Pv) | 0.08 | bar(a) | Absolute pressure
INPUT | Suction Vessel Pressure (Ps_v) | 1.2 | bar(g) | Gauge pressure
INPUT | Discharge Vessel Pressure (Pd_v) | 6.5 | bar(g) | Gauge pressure
INPUT | Rated Flow Rate (Q) | 120 | m3/h | Normal flow + 10% margin
INPUT | Suction Static Head (zs) | 4.5 | m | Height above pump CL
INPUT | Discharge Static Head (zd) | 15 | m | Height above pump CL
INPUT | Suction Friction Loss (hf_s) | 0.8 | m | Includes valves and strainers
INPUT | Discharge Friction Loss (hf_d) | 2.5 | m | Includes valves and piping
CALC | Atmospheric Pressure | 1.0132 | bar | Adjust for altitude
CALC | Total Suction Head (Hs) | 26.2685 | m | Resulting Suction Head
CALC | Total Discharge Head (Hd) | 94.1126 | m | Resulting Discharge Head
CALC | Differential Head (H) | 67.8441 | m | Pump Head Requirement
CALC | Hydraulic Power (Phyd) | 22.185 | kW | Theoretical Power
OUTPUT | Estimated Efficiency (n) | 0.72 | decimal | From manufacturer curve (0.72 = 72%)
OUTPUT | Brake Horsepower (BHP) | 30.8125 | kW | Actual power at shaft
OUTPUT | API 610 Motor Margin | 1.15 | multiplier | 15% margin for 22-55kW range
OUTPUT | Required Motor Rating | 35.4344 | kW | Minimum motor size