## Cover
Electrical Load Calculation — Reusable Template
Engine-driven · real project data · live Excel formulas · fully auditable · reusable across projects
Project
Project | Y-Office Tower — Detailed Design
Board | MDB-OFFICES
Offices | 54
Generated | 2026-07-08T01:30:05
Method — DPS 2022 power-density
Connected load | kVA = Area (m²) × Density (VA/m²) ÷ 1000
Double-height add'l | kVA = (Height − 3.5) × Area × 24 ÷ 1000
Demand | kVA = (Connected + Add'l) × Demand factor
Load-table current | A = Demand × 1000 ÷ 690 → main breaker = next standard size ≥ current
Cable current | A = Demand × 1000 ÷ (√3 × 400)
Cable size | smallest CSA with derated ampacity ≥ current AND VD ≤ 4%
Voltage drop | VD% = Cable current × Length × (mv/a/m) ÷ 1000 ÷ 400 × 100
How to use
It is live | Change any blue input cell on Load-Calc (e.g. an office area) — every yellow formula recomputes automatically.
It is auditable | All standard values (density, demand factor, breaker ladder, cable table) live on the Ref-Tables sheet, each with its source. Formulas reference those cells — edit a reference and the whole calc re-flows.
It is reusable | The workbook is generated from the engine per project — feed a new project's data and you get the same structured workbook.
Legend
Input (extracted / entered)
Calculated (live formula)
Selected output (breaker / cable)

## Load-Calc
Electrical Load Schedule — MDB-OFFICES (DPS 2022 density method) | [14 empty] | live formulas →
Office | Area m² | Height m | Cat | Density VA/m² | Connected kVA | Add'l kVA | Total kVA | DF | Demand kVA | Current A (÷690) | Breaker A | Cable I A | Feeder m | Cable mm² | mv/a/m | VD %
Coffee shop | 197.8 | 7 | C6 | [9 empty] | 55 | 25
Office Double H(38) | 208 | 7 | C7 | [9 empty] | 65 | 25
Office Duplex(37,62) | 169 |  | C7 | [9 empty] | 65 | 10
Office Double H(34,65) | 121 | 7 | C7 | [9 empty] | 80 | 10
Office(39) | 175 |  | C7 | [9 empty] | 80 | 10
Office(54) | 179 |  | C7 | [9 empty] | 85 | 10
Office(84) | 79 |  | C7 | [9 empty] | 90 | 6
Office Duplex(79,112) | 245 |  | C7 | [9 empty] | 90 | 16
Office(86) | 203 |  | C7 | [9 empty] | 75 | 16
Office(82) | 101 |  | C7 | [9 empty] | 75 | 6
Office(111) | 79 |  | C7 | [9 empty] | 95 | 6
Office(113) | 201 |  | C7 | [9 empty] | 80 | 16
Office(99) | 151 |  | C7 | [9 empty] | 80 | 10
Office(127) | 145 |  | C7 | [9 empty] | 100 | 10
Office Double H(128,383) | 200 | 7 | C7 | [9 empty] | 85 | 25
Office Duplex(145,129) | 263 |  | C7 | [9 empty] | 85 | 25
Office(142) | 146 |  | C7 | [9 empty] | 105 | 10
Office(157) | 166 |  | C7 | [9 empty] | 90 | 10
Office Double H(152) | 142 | 7 | C7 | [9 empty] | 110 | 16
Office(175) | 163 |  | C7 | [9 empty] | 95 | 10
Office(370) | 91 |  | C7 | [9 empty] | 120 | 6
Office(379) | 154 |  | C7 | [9 empty] | 105 | 10
Office(377) | 136 |  | C7 | [9 empty] | 120 | 6
Office Duplex(281,359) | 158 |  | C7 | [9 empty] | 110 | 10
Office Double H(283) | 133 | 7 | C7 | [9 empty] | 125 | 16
Office(290) | 136 |  | C7 | [9 empty] | 110 | 6
Office(360) | 135 |  | C7 | [9 empty] | 115 | 6
Office(262) | 92 |  | C7 | [9 empty] | 120 | 6
Office(271) | 133 |  | C7 | [9 empty] | 120 | 6
Office(270) | 129 |  | C7 | [9 empty] | 135 | 6
Office(241) | 127 |  | C7 | [9 empty] | 140 | 6
Office(242) | 131 |  | C7 | [9 empty] | 125 | 6
Office Duplex(247,357) | 158 |  | C7 | [9 empty] | 125 | 10
Office(254) | 125 |  | C7 | [9 empty] | 145 | 6
Office(256) | 128 |  | C7 | [9 empty] | 130 | 6
Office(396) | 126 |  | C7 | [9 empty] | 135 | 6
Office(395) | 123 |  | C7 | [9 empty] | 150 | 10
Office Duplex(393,409) | 158 |  | C7 | [9 empty] | 135 | 10
Office(402) | 99 |  | C7 | [9 empty] | 155 | 6
Office(404) | 124 |  | C7 | [9 empty] | 140 | 6
Office(415) | 92 |  | C7 | [9 empty] | 145 | 6
Office(421) | 99 |  | C7 | [9 empty] | 160 | 6
Office(422) | 122 |  | C7 | [9 empty] | 145 | 6
Office(450) | 74 |  | C7 | [9 empty] | 150 | 6
Office(453) | 142 |  | C7 | [9 empty] | 165 | 10
Office(452) | 69 |  | C7 | [9 empty] | 150 | 6
Office(440) | 74 |  | C7 | [9 empty] | 175 | 6
Office(441) | 136 |  | C7 | [9 empty] | 160 | 10
Office(442) | 64 |  | C7 | [9 empty] | 175 | 6
Office(449) | 74 |  | C7 | [9 empty] | 165 | 6
Office Duplex(448) | 414 |  | C7 | [9 empty] | 180 | 35
Office(33) | 74 |  | C7 | [9 empty] | 170 | 6
Office Duplex(197,415) | 379 |  | C7 | [9 empty] | 175 | 35
Office(430) | 74 |  | C7 | [9 empty] | 175 | 6

## Summary
Board Summary — MDB-OFFICES (OUTPUT)
Feeds transformer sizing, panel schedules and the single-line diagram.
Offices | 54
Total connected |  | kVA
Total additional (double-height) |  | kVA
Total demand |  | kVA
Main incomer current |  | A
Max feeder voltage drop |  | %
⚠ Data-quality flag: Printed board total 846.33216 kVA does not match the sum of 54 row demands (877.369 kVA); difference 31.03684 kVA. Row values are authoritative.

## Ref-Tables
Reference Tables — edit these; the calc recomputes
Values used by the real Y-Tower EL-CAL-5002 load calculation. Indicative — an engineer confirms per project. FLAG: DPS 2022 is a Saudi standard but the project is in Egypt; confirm applicable code with the design office.
Power density (VA/m²) |  |  | DPS 2022 Table 19, p.27
Category | VA/m²
C6 | 188
C7 | 176
Demand factor |  |  | DPS 2022 Table 20, p.29
office | 0.6
Current divisor & voltage
Load-table divisor (÷) | 690 | (Demand×1000/690)
System voltage | 400 | V, L-L
Double-height adder |  |  | DPS 2022, p.26
rate | 24 | VA/m³
standard height | 3.5 | m
Breaker ladder (A) |  |  | DPS 2022 Table 27, p.45
20
30
40
50
70
100
125
150
200
250
300
400
500
600
800
Cable: CSA → mv/a/m & derated ampacity |  |  | EL-CAL-5002 cable sheet mv/a/meter column (fixed per CSA; already includes the 3-phase √3 factor)
CSA mm² | mv/a/m | Derated A
6 | 5.8 | 21
10 | 3.5 | 29
16 | 2.2 | 39
25 | 1.4 | 52
35 | 1.1 | 80