# Panelboard Schedule — Y-Office Tower — Detailed Design

## 1. Method

Real EL-PBS single-phase convention (classification DF + per-circuit breaker/wire).

## 2. Panel roll-ups

| Panel | Total connected VA | Total demand VA | Demand current A | Min main A | Mains A |
| --- | --- | --- | --- | --- | --- |
| EPP-SERVICE-8 | 26946.9 | 21802.2 | 31.47 | 32 | 50 |
| EPP-SERVICE-BS-02 | 3966.3 | 3539.7 | 5.11 | 10 | 20 |

## 3. Circuit selection

| Circuit | Type | Current A | Breaker A | Wire mm² |
| --- | --- | --- | --- | --- |
| Lighting circuit (small) | LTG | 3.2 | 10 | 2.5 |
| Exit sign / emergency | LTG | 0.5 | 10 | 2.5 |
| Motor feed SP-01 | MTR | 13.0 | 16 | 4 |
| ODU motor 20A | MTR | 18.0 | 20 | 6 |
| ODU motor 30A | MTR | 27.0 | 32 | 10 |
| Socket outlet | S.O | 12.0 | 16 | 4 |